## General Info 40001 to 40099
MODBUS Protocol
| Version No. | Revision No.
| 0A | 00
Registers for General (Meter) Information | [7 empty] | Variant
MODBUS Register |  | Parameter | Description | Format |  | Units | Remarks | ELITE 440-441 | ELITE 440-442 | ELITE 440-443 | ELITE 440-444 | ELITE 440-445 | ELITE 440-446 | ELITE 440-447 | ELITE 440-448 | ELITE 440-000
40001 | 40004 | SrNLo | Meter Serial Number | ASCII (8 bytes) | R | NA | Meter Name | Y | Y | Y | Y | Y | Y | Y | Y | Y
40005 | 40008 | SfN | Meter Software Name | ASCII (8 bytes) | R | NA | CLEM Name | Y | Y | Y | Y | Y | Y | Y | Y | Y
40009 | 40012 | FrN1 | FirmWare Name of Module 1 | ASCII (8 bytes) | R | NA |  | N | N | N | N | N | N | Y | Y | Y
40013 | 40016 | FrN2 | FirmWare Name of Module 2 | ASCII (8 bytes) | R | NA |  | N | N | N | N | N | N | Y | Y | Y
40017 | 40017 | Ext_M | IO Card [0=None,1=2I2O,2=4PWM,3=3C1A,4=2C2I] | Unsigned 16 bits | R | NA |  | N | N | N | N | N | N | Y | Y | Y
40018 | 40018 | MBID | Modbus ID | Unsigned 16 bits | R/W | NA |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40019 | 40019 | Pver_rev | Modbus Protocol Version & Revision | Unsigned 16 bits | R | NA |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40020 | 40025 | PrdCd | Product Code | ASCII (12 bytes) | R | NA | Elite440-xyz | Y | Y | Y | Y | Y | Y | Y | Y | Y
40026 | 40027 | Metro LED Pulse Rate | Metro LED Pulse rate in terms of number of counts | 32 bit FP | R | Number of counts per unit increment |  | N | Y | Y | Y | Y | Y | Y | Y | Y
40028 | 40028 | Supported Parameters Energy | Bit 0: Active Total Import Energy Bit 1: Active Total Export Energy Bit 2: Active Import Energy Bit 3: Active Export Energy Bit 4: Reactive - Import While Active Import Energy Bit 5: Reactive - Export While Active Import Energy Bit 6: Reactive - Import While Active Export Energy Bit 7: Reactive - Export While Active Export Energy Bit 8: Apparent - Import Energy Bit 9: Apparent - Export Energy Bit 10: Reactive - Import Energy Bit 11: Reactive - Export Energy Bit 12: Active Forwarded Energy Bit 13: Apparent Forwarded Energy Bit 14: Reactive Lag Forwarded Energy Bit 15: Reactive Lead Forwarded Energy | Unsigned 16 bits | R | NA | NOTE: 1. Respective bit of supported parameter will be set.[Controlled at factory end] 2. Selected Energy parameter is applicable for further selection of MD, Daily Energy Snap and Load Profile. | N | Y | Y | Y | Y | Y | Y | Y | Y
Next Bill Date
40030 | 40031 | Next Bill Date | Next Bill Date | Unsigned 32 bits | R | Seconds Since 1988 |  | N | Y | Y | Y | Y | Y | Y | Y | Y
Meter Type Information
40041 | 40041 | Meter Type | To change the 3W to 4 W application | Unsigned 16 bits | R | NA | 3 = LT, 1= HT4, 2= HT3 (Rest are unused and write has no effect) | Y | Y | Y | Y | Y | Y | Y | Y | Y
Energy Configured parameters
40051 | 40051 | Energy Parameters | Bit mask will be same as mentioned in reg 40028 | Unsigned 16 bits | R | NA |  | N | Y | Y | Y | Y | Y | Y | Y | Y
40052 | 40052 | MD_Params | Bit mask will be based on selected energy in reg 40051 | Unsigned 16 bits | R | NA | While reading, Configured bitmask will be as per the standard list as in Reg 40028. | N | N | N | Y | Y | Y | Y | Y | Y
40058 | 40058 | SIP | Survey Integration Period in minutes | Unsigned 16 bits | R | Minutes | 15,30,60 | Y | Y | Y | Y | Y | Y | Y | Y | Y
40060 | 40060 | Energy parameter BitMask for Load Survey | Bit 0: Active Total Import Energy Bit 1: Active Total Export Energy Bit 2: Active Import Energy Bit 3: Active Export Energy Bit 4: Reactive - Import While Active Import Energy Bit 5: Reactive - Export While Active Import Energy Bit 6: Reactive - Import While Active Export Energy Bit 7: Reactive - Export While Active Export Energy Bit 8: Apparent - Import Energy Bit 9: Apparent - Export Energy Bit 10: Reactive - Import Energy Bit 11: Reactive - Export Energy Bit 12: Active Forwarded Energy Bit 13: Apparent Forwarded Energy Bit 14: Reactive Lag Forwarded Energy Bit 15: Reactive Lead Forwarded Energy | Unsigned 16 bits | R | NA | The respective bit mask of selected Energy parameters are available in reg number 40023 for respective product. (Bits 30-31 are unused and reserved for future use, must be reset) | N | Y | Y | Y | Y | Y | Y | Y | Y
40061 | 40061 | Instantaneous parameter BitMask for Load Survey | 0: R Phase Voltage 1: Y Phase Voltage 2: B Phase Voltage 3: Average Voltage 4: R Phase Current 5: Y Phase Current 6: B Phase Current 7: Average Current 8: R Phase PF 9: Y Phase PF 10: B Phase PF 11: Frequency 12: Counter1 13: Counter2 | Unsigned 16 bits | R | NA |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
Coil Registers
1 |  | Billing Trigger | To Trigger the billing action (Write Only Coil Regs),i.e. MD Reset | Unsigned 16 bits | W |  | 0xFF00 requests the Billing Operation to be started, no other value is valid for this operation | N | N | N | Y | Y | Y | Y | Y | Y
Note: Rest of the registers are reserved.

## Instant Param 40100 to 40199
Registers for Instantaneous Parameters | [7 empty] | Variant
MODBUS Register |  | Parameter | Description | Format | Type | Units | Remarks | ELITE 440-441 | ELITE 440-442 | ELITE 440-443 | ELITE 440-444 | ELITE 440-445 | ELITE 440-446 | ELITE 440-447 | ELITE 440-448 | ELITE 440-000
40100 | 40101 | V1 | R Phase to Neutral Voltage | 32 bit FP | R | Volt |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40102 | 40103 | V2 | Y Phase to Neutral Voltage | 32 bit FP | R | Volt |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40104 | 40105 | V3 | B Phase to Neutral Voltage | 32 bit FP | R | Volt |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40106 | 40107 | Vavg | Average Voltage | 32 bit FP | R | Volt |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40108 | 40109 | V12 | RY Voltage | 32 bit FP | R | Volt |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40110 | 40111 | V23 | YB Voltage | 32 bit FP | R | Volt |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40112 | 40113 | V31 | BR Voltage | 32 bit FP | R | Volt |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40114 | 40115 | L1 | R Phase Line current | 32 bit FP | R | Ampere |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40116 | 40117 | L2 | Y Phase Line current | 32 bit FP | R | Ampere |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40118 | 40119 | L3 | B Phase Line current | 32 bit FP | R | Ampere |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40120 | 40121 | LN | Neutral Line current | 32 bit FP | R | Ampere |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40122 | 40123 | I1 | R Phase Active Current | 32 bit FP | R | Ampere |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40124 | 40125 | I2 | Y Phase Active Current | 32 bit FP | R | Ampere |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40126 | 40127 | I3 | B Phase Active Current | 32 bit FP | R | Ampere |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40128 | 40129 | R1 | R Phase Reactive Current | 32 bit FP | R | Ampere |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40130 | 40131 | R2 | Y Phase Reactive Current | 32 bit FP | R | Ampere |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40132 | 40133 | R3 | B Phase Reactive Current | 32 bit FP | R | Ampere |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40134 | 40135 | Q1 | Power factor | 32 bit FP | R |  | + for Lagging, - for Leading PF | N | Y | Y | Y | Y | Y | Y | Y | Y
40136 | 40137 | Q2 | Power factor | 32 bit FP | R |  | + for Lagging, - for Leading PF | N | Y | Y | Y | Y | Y | Y | Y | Y
40138 | 40139 | Q3 | Power factor | 32 bit FP | R |  | + for Lagging, - for Leading PF | N | Y | Y | Y | Y | Y | Y | Y | Y
40140 | 40141 | QA | Avg power factor | 32 bit FP | R |  | + for Lagging, - for Leading PF | N | Y | Y | Y | Y | Y | Y | Y | Y
40142 | 40143 | KT1 | R- Phase Active Power | 32 bit FP | R | kW |  | N | Y | Y | Y | Y | Y | Y | Y | Y
40144 | 40145 | KT2 | Y- Phase Active Power | 32 bit FP | R | kW |  | N | Y | Y | Y | Y | Y | Y | Y | Y
40146 | 40147 | KT3 | B- Phase Active Power | 32 bit FP | R | kW |  | N | Y | Y | Y | Y | Y | Y | Y | Y
40148 | 40149 | KT | 3 Phase Active Power | 32 bit FP | R | KW |  | N | Y | Y | Y | Y | Y | Y | Y | Y
40150 | 40151 | KV1 | R- Phase Reactive Power | 32 bit FP | R | kVAr |  | N | N | Y | Y | Y | Y | Y | Y | Y
40152 | 40153 | KV2 | Y- Phase Reactive Power | 32 bit FP | R | kVAr |  | N | N | Y | Y | Y | Y | Y | Y | Y
40154 | 40155 | KV3 | B- Phase Reactive Power | 32 bit FP | R | kVAr |  | N | N | Y | Y | Y | Y | Y | Y | Y
40156 | 40157 | KV | 3 Phase Reactive Power | 32 bit FP | R | kVAr |  | N | N | Y | Y | Y | Y | Y | Y | Y
40158 | 40159 | KA1 | R- Phase Apparent Power | 32 bit FP | R | kVA |  | N | N | Y | Y | Y | Y | Y | Y | Y
40160 | 40161 | KA2 | Y- Phase Apparent Power | 32 bit FP | R | kVA |  | N | N | Y | Y | Y | Y | Y | Y | Y
40162 | 40163 | KA3 | B- Phase Apparent Power | 32 bit FP | R | kVA |  | N | N | Y | Y | Y | Y | Y | Y | Y
40164 | 40165 | KA | 3 Phase Apparent Power | 32 bit FP | R | kVA |  | N | N | Y | Y | Y | Y | Y | Y | Y
40166 | 40167 | A12 | RY ph ang | 32 bit FP | R | Degree |  | N | N | Y | Y | Y | Y | Y | Y | Y
40168 | 40169 | A23 | YB ph ang | 32 bit FP | R | Degree |  | N | N | Y | Y | Y | Y | Y | Y | Y
40170 | 40171 | A31 | BR ph ang | 32 bit FP | R | Degree |  | N | N | Y | Y | Y | Y | Y | Y | Y
40172 | 40173 | FQ | Frequency Hz | 32 bit FP | R | Hz |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40174 | 40175 | RT | Meter real Time | Unsigned 32 bits | R/W | Seconds | Time in seconds since 1988 (Time can be set within 2 min offset of current time) | Y | Y | Y | Y | Y | Y | Y | Y | Y
40176 | 40177 | Temperature | Meter Temperature | 32 bit FP | R | Degree Centigrde | Temperature of meter | Y | Y | Y | Y | Y | Y | Y | Y | Y
40178 | 40179 | THDV1 | R-Phase Voltage Total Harmonic Distortion | 32 bit FP | R | % |  | N | N | N | N | N | N | Y | Y | Y
40180 | 40181 | THDV2 | Y-Phase Voltage Total Harmonic Distortion | 32 bit FP | R | % |  | N | N | N | N | N | N | Y | Y | Y
40182 | 40183 | THDV3 | B-Phase Voltage Total Harmonic Distortion | 32 bit FP | R | % |  | N | N | N | N | N | N | Y | Y | Y
40184 | 40185 | THDC1 | R-Phase Current Total Harmonic Distortion | 32 bit FP | R | % |  | N | N | N | N | N | N | Y | Y | Y
40186 | 40187 | THDC2 | Y-Phase Current Total Harmonic Distortion | 32 bit FP | R | % |  | N | N | N | N | N | N | Y | Y | Y
40188 | 40189 | THDC3 | B-Phase Current Total Harmonic Distortion | 32 bit FP | R | % |  | N | N | N | N | N | N | Y | Y | Y
40190 | 40191 | THDP1 | R-Phase Power Total Harmonic Distortion | 32 bit FP | R | % |  | N | N | N | N | N | N | Y | Y | Y
40192 | 40193 | THDP2 | Y-Phase Power Total Harmonic Distortion | 32 bit FP | R | % |  | N | N | N | N | N | N | Y | Y | Y
40194 | 40195 | THDP3 | B-Phase Power Total Harmonic Distortion | 32 bit FP | R | % |  | N | N | N | N | N | N | Y | Y | Y
40196 | 40199 |  | Unused- Reserved

## Recent Param 40200 to 40349
Registers for Recent Parameters
Variant
MODBUS Register |  | Parameter | Description | Format | Type | Units | Remarks | ELITE 440-441 | ELITE 440-442 | ELITE 440-443 | ELITE 440-444 | ELITE 440-445 | ELITE 440-446 | ELITE 440-447 | ELITE 440-448 | ELITE 440-000
Cumulative Energy Parameters
40200 | 40201 | kWhT(I) | Active Total - Import | 32 bit FP | R | kWh |  | N | N | N | N | Y | Y | Y | Y | Y
40202 | 40203 | kWhT(E) | Active Total - Export | 32 bit FP | R | kWh |  | N | N | N | N | Y | Y | Y | Y | Y
40204 | 40205 | kWhT(I) | Active Fundamental - Import | 32 bit FP | R | kWh |  | N | N | N | N | N | N | N | N | Y
40206 | 40207 | kWhT(E) | Active Fundamental - Export | 32 bit FP | R | kWh |  | N | N | N | N | N | N | N | N | Y
40208 | 40209 | kVArh(I)_WI | Reactive - Import While Active Import | 32 bit FP | R | kVArh |  | N | N | N | N | Y | N | Y | N | Y
40210 | 40211 | kVArh(E)_WI | Reactive - Export While Active Import | 32 bit FP | R | kVArh |  | N | N | N | N | Y | N | Y | N | Y
40212 | 40213 | kVArh(I)_WE | Reactive - Import While Active Export | 32 bit FP | R | kVArh |  | N | N | N | N | Y | N | Y | N | Y
40214 | 40215 | kVArh(E)_WE | Reactive - Export While Active Export | 32 bit FP | R | kVArh |  | N | N | N | N | Y | N | Y | N | Y
40216 | 40217 | kVAh(I) | Apparent - Import | 32 bit FP | R | kVAh |  | N | N | N | N | Y | Y | Y | Y | Y
40218 | 40219 | kVAh(E) | Apparent - Export | 32 bit FP | R | kVAh |  | N | N | N | N | Y | Y | Y | Y | Y
40220 | 40221 | kVArh(I) | Reactive - Import (Q1+Q2) | 32 bit FP | R | kVArh |  | N | N | N | N | N | Y | N | Y | Y
40222 | 40223 | kVArh(E) | Reactive - Export (Q3+Q4) | 32 bit FP | R | kVArh |  | N | N | N | N | N | Y | N | Y | Y
40224 | 40225 | kWh (ABS) | Active - Forwarded | 32 bit FP | R | kWh |  | N | Y | Y | Y | N | N | N | N | Y
40226 | 40227 | kVAh(ABS) | Apparent - Forwarded | 32 bit FP | R | kVArh |  | N | Y | Y | Y | N | N | N | N | Y
40228 | 40229 | kWhLag (ABS) | Reactive - Lag Forwarded | 32 bit FP | R | kVArh |  | N | N | Y | Y | N | N | N | N | Y
40230 | 40231 | kWhLead (ABS) | Reactive - Lead Forwarded | 32 bit FP | R | kVAh |  | N | N | Y | Y | N | N | N | N | Y
40232 | 40239 |  | Unused- Reserved
Maximum Demand Parameters (24hr MD)
40240 | 40241 | kWT(I) | Active Total - Import | 32 bit FP | R | kW |  | N | N | N | N | Y | Y | Y | Y | Y
40242 | 40243 | 24hMDTime kWT(I) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | Y | Y | Y | Y | Y
40244 | 40245 | kWT(E) | Active Total - Export | 32 bit FP | R | kW |  | N | N | N | N | Y | Y | Y | Y | Y
40246 | 40247 | 24hMDTime kWT(E) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | Y | Y | Y | Y | Y
40248 | 40249 | kW(I) | Active Fun - Import | 32 bit FP | R | kW |  | N | N | N | N | N | N | N | N | Y
40250 | 40251 | 24hMDTime kW(I) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | N | N | N | N | Y
40252 | 40253 | kW(E) | Active Funl - Export | 32 bit FP | R | kW |  | N | N | N | N | N | N | N | N | Y
40254 | 40255 | 24hMDTime kW(E) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | N | N | N | N | Y
40256 | 40257 | kVAr(I)_WI | Reactive - Import While Active Import | 32 bit FP | R | kVAr |  | N | N | N | N | Y | N | Y | N | Y
40258 | 40259 | 24hMDTime kVAr(I)_WI | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | Y | N | Y | N | Y
40260 | 40261 | kVAr(E)_WI | Reactive -Export While Active Import | 32 bit FP | R | kVAr |  | N | N | N | N | Y | N | Y | N | Y
40262 | 40263 | 24hMDTime kVAr(E)_WI | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | Y | N | Y | N | Y
40264 | 40265 | kVAr(I)_WE | Reactive - Import While Active Export | 32 bit FP | R | kVAr |  | N | N | N | N | Y | N | Y | N | Y
40266 | 40267 | 24hMDTime kVAr(I)_WE | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | Y | N | Y | N | Y
40268 | 40269 | kVAr(E)_WE | Reactive - Export While Active Export | 32 bit FP | R | kVAr |  | N | N | N | N | Y | N | Y | N | Y
40270 | 40271 | 24hMDTime kVAr(E)_WE | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | Y | N | Y | N | Y
40272 | 40273 | kVA(I) | Apparent - Import | 32 bit FP | R | kVA |  | N | N | N | N | Y | Y | Y | Y | Y
40274 | 40275 | 24hMDTime kVA(I) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | Y | Y | Y | Y | Y
40276 | 40277 | kVA(E) | Apparent - Export | 32 bit FP | R | kVA |  | N | N | N | N | Y | Y | Y | Y | Y
40278 | 40279 | 24hMDTime kVA(E) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | Y | Y | Y | Y | Y
40280 | 40281 | kVAr(I) | Reactive - Import | 32 bit FP | R | kVAr |  | N | N | N | N | N | Y | N | Y | Y
40282 | 40283 | 24hMDTime kVAr(I) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | N | Y | N | Y | Y
40284 | 40285 | kVAr(E) | Reactive - Export | 32 bit FP | R | kVAr |  | N | N | N | N | N | Y | N | Y | Y
40286 | 40287 | 24hMDTime kVAr(E) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | N | Y | N | Y | Y
40288 | 40289 | kW(I) ABS | Active - Forwarded | 32 bit FP | R | kW |  | N | Y | Y | Y | N | N | N | N | Y
40290 | 40291 | 24hMDTime kW(I) ABS | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | Y | Y | Y | N | N | N | N | Y
40292 | 40293 | kVA (ABS) | Apparent - Forwarded | 32 bit FP | R | kVAr |  | N | Y | Y | Y | N | N | N | N | Y
40294 | 40295 | 24hMDTime kVA (ABS) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | Y | Y | Y | N | N | N | N | Y
40296 | 40297 | kVAr(I)_Lag (ABS) | Reactive - Lag Forwarded | 32 bit FP | R | kVAr |  | N | N | Y | Y | N | N | N | N | Y
40298 | 40299 | 24hMDTime kVAr(I)_Lag (ABS) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | Y | Y | N | N | N | N | Y
40300 | 40301 | kVAr(I)_Lead (ABS) | Reactive - Lead Forwarded | 32 bit FP | R | kVA |  | N | N | Y | Y | N | N | N | N | Y
40302 | 40303 | 24hMDTime kVAr(I)_Lead (ABS) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | Y | Y | N | N | N | N | Y
40304 | 40319 |  | Unused- Reserved
ON/OFF Parameters
40320 | 40321 | PONMins | Cumulative Power ON Minutes | Unsigned 32 bits | R | Minutes |  | N | N | Y | Y | Y | Y | Y | Y | Y
40322 | 40323 | POFFMins | Cumulative Power OFF Minutes | Unsigned 32 bits | R | Minutes |  | N | N | Y | Y | Y | Y | Y | Y | Y
40324 | 40325 | LON Mins | Cumulative Load ON Minutes | Unsigned 32 bits | R | Minutes |  | N | Y | Y | Y | Y | Y | Y | Y | Y
40326 | 40327 | LOFF Mins | Cumulative Load OFF Minutes | Unsigned 32 bits | R | Minutes |  | N | Y | Y | Y | Y | Y | Y | Y | Y
Pulse Input Counter
40328 | 40329 | Counter1 | Pulse Input Counter 1 | Unsigned 32 bits | R | Counts |  | N | N | N | N | N | N | Y | Y | Y
40330 | 40331 | Counter2 | Pulse Input Counter 2 | Unsigned 32 bits | R | Counts |  | N | N | N | N | N | N | Y | Y | Y
40332 | 40349 |  | Unused- Reserved

## Max-Min Param 40350 to 40519
Registers for Maximima-Minima Parameters
Variant
MODBUS Register |  | Parameter | Description |  |  |  |  | ELITE 440-441 | ELITE 440-442 | ELITE 440-443 | ELITE 440-444 | ELITE 440-445 | ELITE 440-446 | ELITE 440-447 | ELITE 440-448 | ELITE 440-000
|  |  |  | Format | Type | Units | Remarks
40350 | 40351 | VmaxR | Maximum Voltage of R Phase | 32 bit FP | R | Voltage |  | N | N | N | N | N | N | Y | Y | Y
40352 | 40353 | RTVmaxR | Time in seconds since 1988 for Vmax | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40354 | 40355 | VminR | Minimum Voltage of R Phase | 32 bit FP | R | Voltage |  | N | N | N | N | N | N | Y | Y | Y
40356 | 40357 | RTVminR | Time in seconds since 1988 for VminR | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40358 | 40359 | VmaxY | Maximum Voltage of Y Phase | 32 bit FP | R | Voltage |  | N | N | N | N | N | N | Y | Y | Y
40360 | 40361 | RTVmaxY | Time in seconds since 1988 for VmaxY | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40362 | 40363 | VminY | Minimum Voltage of Y Phase | 32 bit FP | R | Voltage |  | N | N | N | N | N | N | Y | Y | Y
40364 | 40365 | RTVminY | Time in seconds since 1988 for VminY | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40366 | 40367 | VmaxB | Maximum Voltage of B Phase | 32 bit FP | R | Voltage |  | N | N | N | N | N | N | Y | Y | Y
40368 | 40369 | RTVmaxB | Time in seconds since 1988 for VmaxB | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40370 | 40371 | VminB | Minimum Voltage of B Phase | 32 bit FP | R | Voltage |  | N | N | N | N | N | N | Y | Y | Y
40372 | 40373 | RTVminB | Time in seconds since 1988 for VminB | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40374 | 40375 | LmaxR | Maximum Line Current of R Phase | 32 bit FP | R | Ampere |  | N | N | N | N | N | N | Y | Y | Y
40376 | 40377 | RTLmaxR | Time in seconds since 1988 for LmaxR | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40378 | 40379 | LminR | Minimum Line Current of R Phase | 32 bit FP | R | Ampere |  | N | N | N | N | N | N | Y | Y | Y
40380 | 40381 | RTLminR | Time in seconds since 1988 for LminR | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40382 | 40383 | LmaxY | Maximum Line Current of Y Phase | 32 bit FP | R | Ampere |  | N | N | N | N | N | N | Y | Y | Y
40384 | 40385 | RTLmaxY | Time in seconds since 1988 for LmaxY | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40386 | 40387 | LminY | Minimum Line Current of Y Phase | 32 bit FP | R | Ampere |  | N | N | N | N | N | N | Y | Y | Y
40388 | 40389 | RTLminY | Time in seconds since 1988 for LminY | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40390 | 40391 | LmaxB | Maximum Line Current of B Phase | 32 bit FP | R | Ampere |  | N | N | N | N | N | N | Y | Y | Y
40392 | 40393 | RTLmaxB | Time in seconds since 1988 for LmaxB | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40394 | 40395 | LminB | Minimum Line Current of B Phase | 32 bit FP | R | Ampere |  | N | N | N | N | N | N | Y | Y | Y
40396 | 40397 | RTLminB | Time in seconds since 1988 for LminB | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40398 | 40399 | PowerActiveMaxR | Maximum Active Power of R Phase | 32 bit FP | R | KW |  | N | N | N | N | N | N | Y | Y | Y
40400 | 40401 | RTPowerActiveMaxR | Time in seconds since 1988 for PowerActiveMaxR | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40402 | 40403 | PowerActiveMinR | Minimum Active Power of R Phase | 32 bit FP | R | KW |  | N | N | N | N | N | N | Y | Y | Y
40404 | 40405 | RTPowerActiveMinR | Time in seconds since 1988 for PowerActiveMinR | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40406 | 40407 | PowerActiveMaxY | Maximum Active Power of Y Phase | 32 bit FP | R | KW |  | N | N | N | N | N | N | Y | Y | Y
40408 | 40409 | RTPowerActiveMaxY | Time in seconds since 1988 for PowerActiveMaxY | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40410 | 40411 | PowerActiveMinY | Minimum Active Power of Y Phase | 32 bit FP | R | KW |  | N | N | N | N | N | N | Y | Y | Y
40412 | 40413 | RTPowerActiveMinY | Time in seconds since 1988 for PowerActiveMinY | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40414 | 40415 | PowerActiveMaxB | Maximum Active Power of B Phase | 32 bit FP | R | KW |  | N | N | N | N | N | N | Y | Y | Y
40416 | 40417 | RTPowerActiveMaxB | Time in seconds since 1988 for PowerActiveMaxB | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40418 | 40419 | PowerActiveMinB | Minimum Active Power of B Phase | 32 bit FP | R | KW |  | N | N | N | N | N | N | Y | Y | Y
40420 | 40421 | RTPowerActiveMinB | Time in seconds since 1988 for PowerActiveMinB | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40422 | 40423 | PowerReactiveMaxR | Maximum Reactive Power of R Phase | 32 bit FP | R | KVAr |  | N | N | N | N | N | N | Y | Y | Y
40424 | 40425 | RTPowerReactiveMaxR | Time in seconds since 1988 for PowerReactiveMaxR | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40426 | 40427 | PowerReactiveMinR | Minimum Reactive Power of R Phase | 32 bit FP | R | KVAr |  | N | N | N | N | N | N | Y | Y | Y
40428 | 40429 | RTPowerReactiveMinR | Time in seconds since 1988 for PowerReactiveMinR | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40430 | 40431 | PowerReactiveMaxY | Maximum Reactive Power of Y Phase | 32 bit FP | R | KVAr |  | N | N | N | N | N | N | Y | Y | Y
40432 | 40433 | RTPowerReactiveMaxY | Time in seconds since 1988 for PowerReactiveMaxY | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40434 | 40435 | PowerReactiveMinY | Minimum Reactive Power of Y Phase | 32 bit FP | R | KVAr |  | N | N | N | N | N | N | Y | Y | Y
40436 | 40437 | RTPowerReactiveMinY | Time in seconds since 1988 for PowerReactiveMinY | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40438 | 40439 | PowerReactiveMaxB | Maximum Reactive Power of B Phase | 32 bit FP | R | KVAr |  | N | N | N | N | N | N | Y | Y | Y
40440 | 40441 | RTPowerReactiveMaxB | Time in seconds since 1988 for PowerReactiveMaxB | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40442 | 40443 | PowerReactiveMinB | Minimum Reactive Power of B Phase | 32 bit FP | R | KVAr |  | N | N | N | N | N | N | Y | Y | Y
40444 | 40445 | RTPowerReactiveMinB | Time in seconds since 1988 for PowerReactiveMinB | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40446 | 40447 | PowerApparentMaxR | Maximum Apparent Power of R Phase | 32 bit FP | R | KVA |  | N | N | N | N | N | N | Y | Y | Y
40448 | 40449 | RTPowerApparentMaxR | Time in seconds since 1988 for PowerApparentMaxR | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40450 | 40451 | PowerApparentMinR | Minimum Apparent Power of R Phase | 32 bit FP | R | KVA |  | N | N | N | N | N | N | Y | Y | Y
40452 | 40453 | RTPowerApparentMinR | Time in seconds since 1988 for PowerApparentMinR | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40454 | 40455 | PowerApparentMaxY | Maximum Apparent Power of Y Phase | 32 bit FP | R | KVA |  | N | N | N | N | N | N | Y | Y | Y
40456 | 40457 | RTPowerApparentMaxY | Time in seconds since 1988 for PowerApparentMaxY | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40458 | 40459 | PowerApparentMinY | Minimum Apparent Power of Y Phase | 32 bit FP | R | KVA |  | N | N | N | N | N | N | Y | Y | Y
40460 | 40461 | RTPowerApparentMinY | Time in seconds since 1988 for PowerApparentMinY | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40462 | 40463 | PowerApparentMaxB | Maximum Apparent Power of B Phase | 32 bit FP | R | KVA |  | N | N | N | N | N | N | Y | Y | Y
40464 | 40465 | RTPowerApparentMaxB | Time in seconds since 1988 for PowerApparentMaxB | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40466 | 40467 | PowerApparentMinB | Minimum Apparent Power of B Phase | 32 bit FP | R | KVA |  | N | N | N | N | N | N | Y | Y | Y
40468 | 40469 | RTPowerApparentMinB | Time in seconds since 1988 for PowerApparentMinB | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40470 | 40471 | PowerFactorMinLagR | Minimum Lagging Power Factor of R Phase | 32 bit FP | R |  |  | N | N | N | N | N | N | Y | Y | Y
40472 | 40473 | RTPowerFactorMinLagR | Time in seconds since 1988 for PowerFactorMinLagR | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40474 | 40475 | PowerFactorMinLeadR | Minimum Leading Power Factor of R Phase | 32 bit FP | R |  |  | N | N | N | N | N | N | Y | Y | Y
40476 | 40477 | RTPowerFactorMinLeadR | Time in seconds since 1988 for PowerFactorMinLeadR | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40478 | 40479 | PowerFactorMinLagY | Minimum Lagging Power Factor of Y Phase | 32 bit FP | R |  |  | N | N | N | N | N | N | Y | Y | Y
40480 | 40481 | RTPowerFactorMinLagY | Time in seconds since 1988 for PowerFactorMinLagY | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40482 | 40483 | PowerFactorMinLeadY | Minimum Leading Power Factor of y Phase | 32 bit FP | R |  |  | N | N | N | N | N | N | Y | Y | Y
40484 | 40485 | RTPowerFactorMinLeadY | Time in seconds since 1988 for PowerFactorMinLeadY | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40486 | 40487 | PowerFactorMinLagB | Minimum Lagging Power Factor of B Phase | 32 bit FP | R |  |  | N | N | N | N | N | N | Y | Y | Y
40488 | 40489 | RTPowerFactorMinLagB | Time in seconds since 1988 for PowerFactorMinLagB | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40490 | 40491 | PowerFactorMinLeadB | Minimum Leading Power Factor of B Phase | 32 bit FP | R |  |  | N | N | N | N | N | N | Y | Y | Y
40492 | 40493 | RTPowerFactorMinLeadB | Time in seconds since 1988 for PowerFactorMinLeadB | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40494 | 40495 | FrequencyMax | Maximum Frequency | 32 bit FP | R | Hz |  | N | N | N | N | N | N | Y | Y | Y
40496 | 40497 | RTFrequencyMax | Time in seconds since 1988 for FrequencyMax | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40498 | 40499 | FrequencyMin | Minimum Frequency | 32 bit FP | R | Hz |  | N | N | N | N | N | N | Y | Y | Y
40500 | 40501 | RTFrequencyMin | Time in seconds since 1988 for FrequencyMin | Unsigned 32 bits | R | Seconds |  | N | N | N | N | N | N | Y | Y | Y
40502 | 40519 |  | Unused- Reserved

## Histories 40520 to 40699
Registers for Energy Histories | [7 empty] | Variant
MODBUS Register |  | Parameter | Description |  |  |  |  | ELITE 440-441 | ELITE 440-442 | ELITE 440-443 | ELITE 440-444 | ELITE 440-445 | ELITE 440-446 | ELITE 440-447 | ELITE 440-448 | ELITE 440-000
|  |  |  | Format | Type | Units | Remarks
40520 | 40520 | History Available | Histories available in meter | 16 Bit Unsigned | R |  |  | N | Y | Y | Y | Y | Y | Y | Y | Y
40521 | 40521 | History Number | History Number to be read | 16 Bit Unsigned | R/W |  |  | N | Y | Y | Y | Y | Y | Y | Y | Y
40522 | 40523 | History Date | History Generation Date | 32 Bit Unsigned | R | Seconds since 1988 |  | N | Y | Y | Y | Y | Y | Y | Y | Y
40524 | 40524 | Supported Energy Mask as per History number | Bit 0: Active Total Import Energy Bit 1: Active Total Export Energy Bit 2: Active Import Energy Bit 3: Active Export Energy Bit 4: Reactive - Import While Active Import Energy Bit 5: Reactive - Export While Active Import Energy Bit 6: Reactive - Import While Active Export Energy Bit 7: Reactive - Export While Active Export Energy Bit 8: Apparent - Import Energy Bit 9: Apparent - Export Energy Bit 10: Reactive - Import Energy Bit 11: Reactive - Export Energy Bit 12: Active Forwarded Energy Bit 13: Apparent Forwarded Energy Bit 14: Reactive Lag Forwarded Energy Bit 15: Reactive Lead Forwarded Energy | 16 Bit Unsigned | R |  |  | N | Y | Y | Y | Y | Y | Y | Y | Y
40525 | 40525 | Supported MD Mask as per History number | Bit 0: Active Total Import Energy Bit 1: Active Total Export Energy Bit 2: Active Import Energy Bit 3: Active Export Energy Bit 4: Reactive - Import While Active Import Energy Bit 5: Reactive - Export While Active Import Energy Bit 6: Reactive - Import While Active Export Energy Bit 7: Reactive - Export While Active Export Energy Bit 8: Apparent - Import Energy Bit 9: Apparent - Export Energy Bit 10: Reactive - Import Energy Bit 11: Reactive - Export Energy Bit 12: Active Forwarded Energy Bit 13: Apparent Forwarded Energy Bit 14: Reactive Lag Forwarded Energy Bit 15: Reactive Lead Forwarded Energy | 16 Bit Unsigned | R |  |  | N | N | N | Y | Y | Y | Y | Y | Y
40526 | 40526 |  | Unused- Reserved
40527 | 40528 | kWhT(I) | Active Total - Import | 32 bit FP | R | kWh |  | N | N | N | N | Y | Y | Y | Y | Y
40529 | 40530 | kWhT(E) | Active Total - Export | 32 bit FP | R | kWh |  | N | N | N | N | Y | Y | Y | Y | Y
40531 | 40532 | kWhT(I) | Active Fundamental - Import | 32 bit FP | R | kWh |  | N | N | N | N | N | N | N | N | Y
40533 | 40534 | kWhT(E) | Active Fundamental - Export | 32 bit FP | R | kWh |  | N | N | N | N | N | N | N | N | Y
40535 | 40536 | kVArh(I)_WI | Reactive - Import While Active Import | 32 bit FP | R | kVArh |  | N | N | N | N | Y | N | Y | N | Y
40537 | 40538 | kVArh(E)_WI | Reactive - Export While Active Import | 32 bit FP | R | kVArh |  | N | N | N | N | Y | N | Y | N | Y
40539 | 40540 | kVArh(I)_WE | Reactive - Import While Active Export | 32 bit FP | R | kVArh |  | N | N | N | N | Y | N | Y | N | Y
40541 | 40542 | kVArh(E)_WE | Reactive - Export While Active Export | 32 bit FP | R | kVArh |  | N | N | N | N | Y | N | Y | N | Y
40543 | 40544 | kVAh(I) | Apparent - Import | 32 bit FP | R | kVAh |  | N | N | N | N | Y | Y | Y | Y | Y
40545 | 40546 | kVAh(E) | Apparent - Export | 32 bit FP | R | kVAh |  | N | N | N | N | Y | Y | Y | Y | Y
40547 | 40548 | kVArh(I) | Reactive - Import (Q1+Q2) | 32 bit FP | R | kVArh |  | N | N | N | N | N | Y | N | Y | Y
40549 | 40550 | kVArh(E) | Reactive - Export (Q3+Q4) | 32 bit FP | R | kVArh |  | N | N | N | N | N | Y | N | Y | Y
40551 | 40552 | kWh (ABS) | Active - Forwarded | 32 bit FP | R | kWh |  | N | Y | Y | Y | N | N | N | N | Y
40553 | 40554 | kVAh(ABS) | Apparent - Forwarded | 32 bit FP | R | kVArh |  | N | Y | Y | Y | N | N | N | N | Y
40555 | 40556 | kWhLag (ABS) | Reactive - Lag Forwarded | 32 bit FP | R | kVArh |  | N | N | Y | Y | N | N | N | N | Y
40557 | 40558 | kWhLead (ABS) | Reactive - Lead Forwarded | 32 bit FP | R | kVAh |  | N | N | Y | Y | N | N | N | N | Y
40559 | 40569 |  | Unused- Reserved
Maximum Demand History (24 Hr MD i.e.UMD)
40570 | 40571 | kWT(I) | Active Total - Import | 32 bit FP | R | kWh |  | N | N | N | N | Y | Y | Y | Y | Y
40572 | 40573 | 24hMDTime kWT(I) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | Y | Y | Y | Y | Y
40574 | 40575 | kWT(E) | Active Total - Export | 32 bit FP | R | kWh |  | N | N | N | N | Y | Y | Y | Y | Y
40576 | 40577 | 24hMDTime kWT(E) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | Y | Y | Y | Y | Y
40578 | 40579 | kW(I) | Active Fun - Import | 32 bit FP | R | kWh |  | N | N | N | N | N | N | N | N | Y
40580 | 40581 | 24hMDTime kW(I) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | N | N | N | N | Y
40582 | 40583 | kW(E) | Active Funl - Export | 32 bit FP | R | kWh |  | N | N | N | N | N | N | N | N | Y
40584 | 40585 | 24hMDTime kW(E) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | N | N | N | N | Y
40586 | 40587 | kVAr(I)_WI | Reactive - Import While Active Import | 32 bit FP | R | kVArh |  | N | N | N | N | Y | N | Y | N | Y
40588 | 40589 | 24hMDTime kVAr(I)_WI | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | Y | N | Y | N | Y
40590 | 40591 | kVAr(E)_WI | Reactive -Export While Active Import | 32 bit FP | R | kVArh |  | N | N | N | N | Y | N | Y | N | Y
40592 | 40593 | 24hMDTime kVAr(E)_WI | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | Y | N | Y | N | Y
40594 | 40595 | kVAr(I)_WE | Reactive - Import While Active Export | 32 bit FP | R | kVArh |  | N | N | N | N | Y | N | Y | N | Y
40596 | 40597 | 24hMDTime kVAr(I)_WE | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | Y | N | Y | N | Y
40598 | 40599 | kVAr(E)_WE | Reactive - Export While Active Export | 32 bit FP | R | kVArh |  | N | N | N | N | Y | N | Y | N | Y
40600 | 40601 | 24hMDTime kVAr(E)_WE | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | Y | N | Y | N | Y
40602 | 40603 | kVA(I) | Apparent - Import | 32 bit FP | R | kVAh |  | N | N | N | N | Y | Y | Y | Y | Y
40604 | 40605 | 24hMDTime kVA(I) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | Y | Y | Y | Y | Y
40606 | 40607 | kVA(E) | Apparent - Export | 32 bit FP | R | kVAh |  | N | N | N | N | Y | Y | Y | Y | Y
40608 | 40609 | 24hMDTime kVA(E) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | Y | Y | Y | Y | Y
40610 | 40611 | kVAr(I) | Reactive - Import | 32 bit FP | R | kVArh |  | N | N | N | N | N | Y | N | Y | Y
40612 | 40613 | 24hMDTime kVAr(I) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | N | Y | N | Y | Y
40614 | 40615 | kVAr(E) | Reactive - Export | 32 bit FP | R | kVArh |  | N | N | N | N | N | Y | N | Y | Y
40616 | 40617 | 24hMDTime kVAr(E) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | N | N | Y | N | Y | Y
40618 | 40619 | kW(I) ABS | Active - Forwarded | 32 bit FP | R | kW |  | N | N | N | Y | N | N | N | N | Y
40620 | 40621 | 24hMDTime kW(I) ABS | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | Y | N | N | N | N | Y
40622 | 40623 | kVA (ABS) | Apparent - Forwarded | 32 bit FP | R | kVAr |  | N | N | N | Y | N | N | N | N | Y
40624 | 40625 | 24hMDTime kVA (ABS) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | Y | N | N | N | N | Y
40626 | 40627 | kVAr(I)_Lag (ABS) | Reactive - Lag Forwarded | 32 bit FP | R | kVAr |  | N | N | N | Y | N | N | N | N | Y
40628 | 40629 | 24hMDTime kVAr(I)_Lag (ABS) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | Y | N | N | N | N | Y
40630 | 40631 | kVAr(I)_Lead (ABS) | Reactive - Lead Forwarded | 32 bit FP | R | kVA |  | N | N | N | Y | N | N | N | N | Y
40632 | 40633 | 24hMDTime kVAr(I)_Lead (ABS) | 24h MD Date & Time Stamp | Unsigned 32 bits | R | Seconds | Seconds Since 1988 | N | N | N | Y | N | N | N | N | Y
40634 | 40639 |  | Unused- Reserved
Cummulative CMD
40640 | 40641 | CMD_kWhT(I) | Active Total - Import | 32 bit FP | R | kW |  | N | N | N | N | Y | Y | Y | Y | Y
40642 | 40643 | CMD_kWhT(E) | Active Total - Export | 32 bit FP | R | kW |  | N | N | N | N | Y | Y | Y | Y | Y
40644 | 40645 | CMD_kWhT(I) | Active Fundamental - Import | 32 bit FP | R | kW |  | N | N | N | N | N | N | N | N | Y
40646 | 40647 | CMD_kWhT(E) | Active Fundamental - Export | 32 bit FP | R | kW |  | N | N | N | N | N | N | N | N | Y
40648 | 40649 | CMD_kVArh(I)_WI | Reactive - Import While Active Import | 32 bit FP | R | kVAr |  | N | N | N | N | Y | N | Y | N | Y
40650 | 40651 | CMD_kVArh(E)_WI | Reactive - Export While Active Import | 32 bit FP | R | kVAr |  | N | N | N | N | Y | N | Y | N | Y
40652 | 40653 | CMD_kVArh(I)_WE | Reactive - Import While Active Export | 32 bit FP | R | kVAr |  | N | N | N | N | Y | N | Y | N | Y
40654 | 40655 | CMD_kVArh(E)_WE | Reactive - Export While Active Export | 32 bit FP | R | kVAr |  | N | N | N | N | Y | N | Y | N | Y
40656 | 40657 | CMD_kVAh(I) | Apparent - Import | 32 bit FP | R | kVA |  | N | N | N | N | Y | Y | Y | Y | Y
40658 | 40659 | CMD_kVAh(E) | Apparent - Export | 32 bit FP | R | kVA |  | N | N | N | N | Y | Y | Y | Y | Y
40660 | 40661 | CMD_kVArh(I) | Reactive - Import | 32 bit FP | R | kVAr |  | N | N | N | N | N | Y | N | Y | Y
40662 | 40663 | CMD_kVArh(E) | Reactive - Export | 32 bit FP | R | kVAr |  | N | N | N | N | N | Y | N | Y | Y
40664 | 40665 | CMD_kW(I) ABS | Active - Forwarded | 32 bit FP | R | kW |  | N | N | N | Y | N | N | N | N | Y
40666 | 40667 | CMD_kVA (ABS) | Apparent - Forwarded | 32 bit FP | R | kVAr |  | N | N | N | Y | N | N | N | N | Y
40668 | 40669 | CMD_kVAr(I)_Lag(ABS) | Reactive - Lag Forwarded | 32 bit FP | R | kVAr |  | N | N | N | Y | N | N | N | N | Y
40670 | 40671 | CMD_kVAr(I)_Lead(ABS) | Reactive - Lead Forwarded | 32 bit FP | R | kVA |  | N | N | N | Y | N | N | N | N | Y
40672 | 40679 |  | Unused- Reserved
Other Param
40680 | 40681 | PONMins | Cumulative Power ON Minutes | Unsigned 32 bits | R | Minutes |  | N | N | Y | Y | Y | Y | Y | Y | Y
40682 | 40683 | POFFMins | Cumulative Power OFF Minutes | Unsigned 32 bits | R | Minutes |  | N | N | Y | Y | Y | Y | Y | Y | Y
40684 | 40685 | LON Mins | Cumulative Load ON Minutes | Unsigned 32 bits | R | Minutes |  | N | Y | Y | Y | Y | Y | Y | Y | Y
40686 | 40687 | LOFF Mins | Cumulative Load OFF Minutes | Unsigned 32 bits | R | Minutes |  | N | Y | Y | Y | Y | Y | Y | Y | Y
40688 | 40699 |  | Unused- Reserved

## Daily Snaps 40700 - 40749
Registers for Daily Energy Snapshots | [7 empty] | Variant
MODBUS Register |  | Parameter | Description |  |  |  |  | ELITE 440-441 | ELITE 440-442 | ELITE 440-443 | ELITE 440-444 | ELITE 440-445 | ELITE 440-446 | ELITE 440-447 | ELITE 440-448 | ELITE 440-000
|  |  |  | Format | Type | Units | Remarks
40700 | 40700 | Available Snapshots | Snapshots available in the meter | 16 Bit Unsigned | R |  |  | N | Y | Y | Y | Y | Y | Y | Y | Y
40701 | 40701 | Snap shot number | 0 means last snapshot | 16 Bit Unsigned | R/W |  | Default Set to zero (i.e. Last day end snap value to be read) | N | Y | Y | Y | Y | Y | Y | Y | Y
40702 | 40703 | Time of snapshot | Seconds since 1988 | 32 Bit Unsigned | R | Seconds |  | N | Y | Y | Y | Y | Y | Y | Y | Y
40704 | 40704 | Daily Energy Parameter Mask as per Snapshot number | Bit 0: Active Total Import Energy Bit 1: Active Total Export Energy Bit 2: Active Import Energy Bit 3: Active Export Energy Bit 4: Reactive - Import While Active Import Energy Bit 5: Reactive - Export While Active Import Energy Bit 6: Reactive - Import While Active Export Energy Bit 7: Reactive - Export While Active Export Energy Bit 8: Apparent - Import Energy Bit 9: Apparent - Export Energy Bit 10: Reactive - Import Energy Bit 11: Reactive - Export Energy Bit 12: Active Forwarded Energy Bit 13: Apparent Forwarded Energy Bit 14: Reactive Lag Forwarded Energy Bit 15: Reactive Lead Forwarded Energy | 16 Bit Unsigned | R |  |  | N | Y | Y | Y | Y | Y | Y | Y | Y
40705 | 40709 |  | Unused- Reserved
40710 | 40711 | kWhT(I) | Active Total - Import | 32 bit FP | R | kWh |  | N | N | N | N | Y | Y | Y | Y | Y
40712 | 40713 | kWhT(E) | Active Total - Export | 32 bit FP | R | kWh |  | N | N | N | N | Y | Y | Y | Y | Y
40714 | 40715 | kWhT(I) | Active Fundamental - Import | 32 bit FP | R | kWh |  | N | N | N | N | N | N | N | N | Y
40716 | 40717 | kWhT(E) | Active Fundamental - Export | 32 bit FP | R | kWh |  | N | N | N | N | N | N | N | N | Y
40718 | 40719 | kVArh(I)_WI | Reactive - Import While Active Import | 32 bit FP | R | kVArh |  | N | N | N | N | Y | N | Y | N | Y
40720 | 40721 | kVArh(E)_WI | Reactive - Export While Active Import | 32 bit FP | R | kVArh |  | N | N | N | N | Y | N | Y | N | Y
40722 | 40723 | kVArh(I)_WE | Reactive - Import While Active Export | 32 bit FP | R | kVArh |  | N | N | N | N | Y | N | Y | N | Y
40724 | 40725 | kVArh(E)_WE | Reactive - Export While Active Export | 32 bit FP | R | kVArh |  | N | N | N | N | Y | N | Y | N | Y
40726 | 40727 | kVAh(I) | Apparent - Import | 32 bit FP | R | kVAh |  | N | N | N | N | Y | Y | Y | Y | Y
40728 | 40729 | kVAh(E) | Apparent - Export | 32 bit FP | R | kVAh |  | N | N | N | N | Y | Y | Y | Y | Y
40730 | 40731 | kVArh(I) | Reactive - Import | 32 bit FP | R | kVArh |  | N | N | N | N | N | Y | N | Y | Y
40732 | 40733 | kVArh(E) | Reactive - Export | 32 bit FP | R | kVArh |  | N | N | N | N | N | Y | N | Y | Y
40734 | 40735 | kWh (ABS) | Active - Forwarded | 32 bit FP | R | kWh |  | N | Y | Y | Y | N | N | N | N | Y
40736 | 40737 | kVAh(ABS) | Apparent - Forwarded | 32 bit FP | R | kVArh |  | N | Y | Y | Y | N | N | N | N | Y
40738 | 40739 | kWhLag (ABS) | Reactive - Lag Forwarded | 32 bit FP | R | kVArh |  | N | N | Y | Y | N | N | N | N | Y
40740 | 40741 | kWhLead (ABS) | Reactive - Lead Forwarded | 32 bit FP | R | kVAh |  | N | N | Y | Y | N | N | N | N | Y
40742 | 40749 |  | Unused- Reserved

## Miscellaneous 40750-40769
Miscellaneous Registers
Variant
MODBUS Register |  | Parameter | Description | Format | Type | Units | Remarks | ELITE 440-441 | ELITE 440-442 | ELITE 440-443 | ELITE 440-444 | ELITE 440-445 | ELITE 440-446 | ELITE 440-447 | ELITE 440-448 | ELITE 440-000
40750 | 40751 | Flags *** | Event Status | Unsigned 32bits | R |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40752 | 40753 | Last OCC Evt | Last Occ Event | Unsigned 32bits | R | Bit Mask as mentioned below |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40754 | 40755 | Last OCC Evt Tm | Last Occ Event Time | Unsigned 32bits | R | Time in Seconds Since 1988 |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40756 | 40756 | Special Flags **** | Special Events Status | Unsigned 16bits | R |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40757 | 40769 |  | Unused- Reserved
Note: Applicable for all the variants
Bit number | Format | Flags ***
0 | bit | R-Phase Voltage missing
1 | bit | Y-Phase Voltage missing
2 | bit | B-Phase Voltage missing
3 | bit | Invalid Voltage
4 | bit | Voltage Imbalance
5 | bit | High Voltage
6 | bit | Low Voltage
7 | bit | R-Phase CT reverse
8 | bit | Y-Phase CT reverse
9 | bit | B-Phase CT reverse
10 | bit | Low power factor
11 | bit | Invalid Phase Association
12 | bit | Over Load
13 | bit | Under Load
14 | bit | Current Imbalance
15 | bit | Module Card Unplugged
16 to 31 | bit | Not used
Bit number | Format | Special Flags ****
0 | bit | Battery fail
1 | bit | NVRAM fail
2 | bit | NVM Fail
3 to 15 | bit | Not used

## Configurable Regs 40770 - 40799
Configurable Registers
Variant
MODBUS Register |  | Parameter | Description | Format | Type | Units | Remarks | ELITE 440-441 | ELITE 440-442 | ELITE 440-443 | ELITE 440-444 | ELITE 440-445 | ELITE 440-446 | ELITE 440-447 | ELITE 440-448 | ELITE 440-000
40770
40770 | 40799 |  | Unused- Reserved

## SIP Data 40800 to 40999
Registers for Data Logging Information
Variant
MODBUS Register |  | Parameter | Description | Format | Type | Remarks | ELITE 440-441 | ELITE 440-442 | ELITE 440-443 | ELITE 440-444 | ELITE 440-445 | ELITE 440-446 | ELITE 440-447 | ELITE 440-448 | ELITE 440-000
40800 | 40800 | Data Logging Days Available | Active LS Days available |  | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40801 | 40801 | SIP Config Indices | 0: Active Total Import Energy 1: Active Total Export Energy 2: Active Import Energy 3: Active Export Energy 4: Reactive - Import While Active Import Energy 5: Reactive - Export While Active Import Energy 6: Reactive - Import While Active Export Energy 7: Reactive - Export While Active Export Energy 8: Apparent - Import Energy 9: Apparent - Export Energy 10: Reactive - Import Energy 11: Reactive - Export Energy 12: Active Forwarded Energy 13: Apparent Forwarded Energy 14: Reactive Lag Forwarded Energy 15: Reactive Lead Forwarded Energy | Unsigned 16 bits | R/W | Parameter index To be Read (Default 00 i.e. Active Import) | Y | Y | Y | Y | Y | Y | Y | Y | Y
|  |  | 16: R Phase Voltage 17: Y Phase Voltage 18: B Phase Voltage 19: Average Voltage 20: R Phase Current 21: Y Phase Current 22: B Phase Current 23: Average Current 24: R Phase PF 25: Y Phase PF 26: B Phase PF 27: Frequency 28: Counter1 29: Counter2 |  |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40802 | 40802 | Day Number | 1 for Previous; 0 for current | Unsigned 16 bits | R/W | Default zero (i.e. current day) | Y | Y | Y | Y | Y | Y | Y | Y | Y
40803 | 40803 |  | Unused- Reserved
40804 | 40805 | Date | Load Survey Date of the corresponding day no. | Unsigned 32 bits | R | Secs Since 1988 | Y | Y | Y | Y | Y | Y | Y | Y | Y
40806 | 40807 |  | Unused- Reserved
40808 | 40809 | SIP 1 | 1st SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40810 | 40811 | SIP 2 | 2nd SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40812 | 40813 | SIP 3 | 3rd SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40814 | 40815 | SIP 4 | 4th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40816 | 40817 | SIP 5 | 5th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40818 | 40819 | SIP 6 | 6th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40820 | 40821 | SIP 7 | 7th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40822 | 40823 | SIP 8 | 8th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40824 | 40825 | SIP 9 | 9th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40826 | 40827 | SIP 10 | 10th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40828 | 40829 | SIP 11 | 11th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40830 | 40831 | SIP 12 | 12th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40832 | 40833 | SIP 13 | 13th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40834 | 40835 | SIP 14 | 14th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40836 | 40837 | SIP 15 | 15th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40838 | 40839 | SIP 16 | 16th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40840 | 40841 | SIP 17 | 17th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40842 | 40843 | SIP 18 | 18th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40844 | 40845 | SIP 19 | 19th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40846 | 40847 | SIP 20 | 20th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40848 | 40849 | SIP 21 | 21th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40850 | 40851 | SIP 22 | 22th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40852 | 40853 | SIP 23 | 23th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40854 | 40855 | SIP 24 | 24th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40856 | 40857 | SIP 25 | 25th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40858 | 40859 | SIP 26 | 26th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40860 | 40861 | SIP 27 | 27th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40862 | 40863 | SIP 28 | 28th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40864 | 40865 | SIP 29 | 29th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40866 | 40867 | SIP 30 | 30th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40868 | 40869 | SIP 31 | 31th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40870 | 40871 | SIP 32 | 32th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40872 | 40873 | SIP 33 | 33th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40874 | 40875 | SIP 34 | 34th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40876 | 40877 | SIP 35 | 35th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40878 | 40879 | SIP 36 | 36th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40880 | 40881 | SIP 37 | 37th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40882 | 40883 | SIP 38 | 38th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40884 | 40885 | SIP 39 | 39th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40886 | 40887 | SIP 40 | 40th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40888 | 40889 | SIP 41 | 41th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40890 | 40891 | SIP 42 | 42th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40892 | 40893 | SIP 43 | 43th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40894 | 40895 | SIP 44 | 44th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40896 | 40897 | SIP 45 | 45th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40898 | 40899 | SIP 46 | 46th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40900 | 40901 | SIP 47 | 47th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40902 | 40903 | SIP 48 | 48th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40904 | 40905 | SIP 49 | 49th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40906 | 40907 | SIP 50 | 50th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40908 | 40909 | SIP 51 | 51th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40910 | 40911 | SIP 52 | 52th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40912 | 40913 | SIP 53 | 53th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40914 | 40915 | SIP 54 | 54th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40916 | 40917 | SIP 55 | 55th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40918 | 40919 | SIP 56 | 56th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40920 | 40921 | SIP 57 | 57th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40922 | 40923 | SIP 58 | 58th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40924 | 40925 | SIP 59 | 59th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40926 | 40927 | SIP 60 | 60th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40928 | 40929 | SIP 61 | 61th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40930 | 40931 | SIP 62 | 62th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40932 | 40933 | SIP 63 | 63th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40934 | 40935 | SIP 64 | 64th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40936 | 40937 | SIP 65 | 65th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40938 | 40939 | SIP 66 | 66th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40940 | 40941 | SIP 67 | 67th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40942 | 40943 | SIP 68 | 68th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40944 | 40945 | SIP 69 | 69th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40946 | 40947 | SIP 70 | 70th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40948 | 40949 | SIP 71 | 71th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40950 | 40951 | SIP 72 | 72th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40952 | 40953 | SIP 73 | 73th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40954 | 40955 | SIP 74 | 74th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40956 | 40957 | SIP 75 | 75th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40958 | 40959 | SIP 76 | 76th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40960 | 40961 | SIP 77 | 77th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40962 | 40963 | SIP 78 | 78th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40964 | 40965 | SIP 79 | 79th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40966 | 40967 | SIP 80 | 80th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40968 | 40969 | SIP 81 | 81th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40970 | 40971 | SIP 82 | 82th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40972 | 40973 | SIP 83 | 83th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40974 | 40975 | SIP 84 | 84th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40976 | 40977 | SIP 85 | 85th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40978 | 40979 | SIP 86 | 86th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40980 | 40981 | SIP 87 | 87th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40982 | 40983 | SIP 88 | 88th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40984 | 40985 | SIP 89 | 89th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40986 | 40987 | SIP 90 | 90th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40988 | 40989 | SIP 91 | 91th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40990 | 40991 | SIP 92 | 92th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40992 | 40993 | SIP 93 | 93th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40994 | 40995 | SIP 94 | 94th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40996 | 40997 | SIP 95 | 95th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
40998 | 40999 | SIP 96 | 96th SIP Since Midnight | 32 bit FP | R |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
Note: It is proposed that while reading SIP data should be read by setting the "SIP Config. Index" & "Day Number" every time while reading

## Revision History
Version | Date | Modified By | Revision History
001 | 31/10/2011 | Daood Ahmad | Initial Version for IIIrd Party Interface
002 | 2012-01-16 | Kamal Prajapati | 1. Variant wise applicability of each registers mentioned.